## General Site Conditions
General Conditions
Waterproofing Applicator agency shall provide minimum 10 years Warranty for waterproofing sytem as per Technical data sheets / specifications / SOP's duly approved by Engineering Incharge, from the date of issue of Virtual completion certificate
Contractor shall ensure proper access shall be given to the applicator agency in case of any leakages for rectifications.
The Contractor shall ensure that the surface handed over to the application agency shall be cleaned properly, free of major undulations, depressions to be filled as per manufacturer methodology submitted and to the satisfaction of Engineering Incharge.
Approved Waterproofing manufacturer has to provide supporting technical submittals, calculations along with the bid submission. Approvals and go ahead by the Engineering Incharge on methodology is a must to proceed further.
Manufacturer shall share the compliance certificate as per specifications & also share third party test and Data sheet shall have minimum specified range. Any deviation from the specifications will have financial concequency
Products used by the contractors to be of low VOC and in line with IGBC requirements.
Consumption of waterproofing shall be established at site and third party, manufacturer shall share density, solild content data in MTC & TDS.
The Client has provided reuirement for the preferred waterproofing methods for the items listed in this BoQ, the Contractor is expected to propose a suitable water proofing method and provided detailed item description, Work Method Statement, Product Details of the proposed materials along with their technical details with the proposal.

## Specifications Clauses
General Specification Clause
Location : Swimming Pools
2K Cementitious Waterproofing : Positive Waterproofing
Supplying and applying waterproofing treatment using a two-component polymer-modified cementitious elastomeric membrane, mixed on site and applied in two to three coats by brush/roller over a prepared substrate, to achieve a DFT ≥1.0 mm. The system shall be flexible (elongation ≥40%), crack-bridging ≥0.6 mm, and suitable for permanent water immersion and potable water use. The system shall bond well with cementitious tile adhesives, making it ideal for swimming pool shells (both basement pools and podium pools). Item rate shall include complete surface preparation, priming (if specified), joint treatment, membrane application, QA/QC testing, and guarantee. Mode of Measurement: Net surface area of pool shell treated; overlaps deemed included.
HDPE Pre-applied Membrane – Swimming Pool Waterproofing (Only Basement & Confined Pools)
Supplying and installing a fully bonded pre-applied HDPE waterproofing membrane (≥1.2 mm thick) with pressure-sensitive adhesive layer and removable release liner, applied on the prepared substrate of swimming pool basements (confined areas) before casting RCC shell. The HDPE sheet shall be fully bonded to the poured concrete, preventing lateral water migration, and shall remain durable under permanent hydrostatic pressure. Joints shall be treated with minimum 75–80 mm overlaps, sealed with double-sided adhesive tape, and termination details as per manufacturer’s specifications. The item rate shall include substrate preparation (blinding concrete, smoothening, cleaning), installation of membrane sheets with overlaps, treatment of corners/junctions, pipe penetrations, protection works, QA/QC checks, and provision of a 10-year waterproofing guarantee. Mode of Measurement: Net pool shell area waterproofed; laps included in rate.

## BOQ Items
BILL OF QUANTITY
| Items | Unit | Quantity | Unit Rate (INR) | Amount (INR)
Location : Swimming Pools
2K Cementitious Waterproofing : Positive Waterproofing
1.1 | Surface preparation: smoothening of RCC shell, removal of laitance, sharp edges, cleaning with water jet. | SQM | 0 | 0 | 0
1.2 | Treatment of cracks/joints with polymer-modified repair mortar. | SQM | 0 | 0 | 0
1.3 | Supplying and applying two-component cementitious elastomeric membrane in 2–3 coats by brush/roller, at coverage 2.0 kg/m² to achieve DFT ≥1.0 mm. | SQM | 0 | 0 | 0
1.4 | Fillet treatment (50×50 mm) at internal corners with cementitious mortar + membrane. | SQM | 0 | 0 | 0
1.5 | Protection: screed ≥100 mm with slope | SQM | 0 | 0 | 0
HDPE Pre-applied Membrane – Swimming Pool Waterproofing (Only Basement & Confined Pools)
2.1 | Surface preparation: blinding concrete (≥50 mm thick), smoothened & dried surface. | SQM | 0 | 0 | 0
2.2 | Supply & installation of HDPE pre-applied waterproofing membrane (≥1.2 mm) with selvedge laps (≥75 mm). | SQM | 0 | 0 | 0
2.3 | Joint treatment with double-sided adhesive tape & firm rolling for sealing. | SQM | 0 | 0 | 0
2.4 | Treatment at corners, edges, & pipe penetrations with extra membrane reinforcement. | SQM | 0 | 0 | 0
2.5 | Protection works during reinforcement fixing & concreting.

## Reference Standards
Reference Standards
Location : Podiums
Standard | Detail | Note
ASTM D 412 | Tensile Strength & Elongation: | Measures flexibility and crack-bridging capacity of membranes.
EN 12390-8/ ASTM D5385 | Water penetration under pressure/ Hydrostatic pressure resistance. | Evaluates ability of waterproofing to resist water penetration under pressure.
ASTM C836 | Liquid-Applied Membranes: | Specifies performance criteria for cold, liquid-applied waterproofing systems.
ASTM D4541/ ASTM D7234 | Adhesion strength (pull-off) |  | –
BS 6920 | Suitability for contact with potable water.
EN 14891 | Crack bridging under standard conditions.

## Performance Parameters
Performance Standard
Location : Swimming Pool Waterproofing
Product : 2K Cementitious Waterproofing
Property | Requirement | Standard
Elongation | ≥40% | ASTM D412
Tensile Strength | ≥0.7 MPa | ASTM D412
Crack Bridging | ≥0.7 mm | EN 14891
Adhesion to Concrete | ≥1.0 MPa | ASTM D7234
Water Penetration | No penetration @ 5 bar | EN 12390-8
Potable Water Safety | Pass | BS 6920/ CFTRI
Product : HDPE bonded Membrane [Basement & Confined Pools]
Property | Requirement | Standard
Thickness | ≥1.2 mm | ASTM D751
Tensile Strength | ≥25 MPa | ASTM D412
Elongation | ≥400% | ASTM D412
Peel Adhesion to Concrete | ≥1.5 N/mm | ASTM D903
Puncture Resistance | ≥1000 N | ASTM E154
Hydrostatic Pressure Resistance | ≥70 m head | ASTM D5385
UV Resistance | No blistering/cracking after 1000 hrs | ASTM G154

## Checklist
Checklist
Location : Podium Waterproofing
Product : 2K Cementitious Waterproofing
S No | Description | Yes | No
RCC pool shell strength ≥M25, cured ≥28 days.
Surface cleaned of laitance, oil, loose material.
Honeycombs, cracks, joints repaired with non-shrink mortar.
Fillets (50×50 mm) applied at all corners and junctions.
Membrane applied in 2–3 coats, cross-directional, DFT ≥1.0 mm.
Adhesion test ≥1.0 MPa passed.
Pond test (7 days full water storage) completed and approved.
Tiles applied only after waterproofing system is cured and accepted.
QA/QC reports documented; 10-year guarantee issued.
Product : HDPE bonded Membrane [Basement & Confined Pools]
S No | Description | Yes | No
Blinding PCC laid smooth & cured, free from laitance.
Surface cleaned and dried before membrane placement.
Membrane sheets laid with ≥75 mm overlaps, sealed with double-sided tape.
Corners, terminations, penetrations treated with reinforcement detailing.
Concreting placed directly on bonded HDPE with no displacement.
QA/QC: peel adhesion ≥1.5 N/mm, hydrostatic test ≥70 m head.
Documentation & guarantee submitted.