## General Site Conditions
General Conditions
Waterproofing Applicator agency shall provide minimum 10 years Warranty for waterproofing sytem as per Technical data sheets / specifications / SOP's duly approved by Engineering Incharge, from the date of issue of Virtual completion certificate
Contractor shall ensure proper access shall be given to the applicator agency in case of any leakages for rectifications.
The Contractor shall ensure that the surface handed over to the application agency shall be cleaned properly, free of major undulations, depressions to be filled as per manufacturer methodology submitted and to the satisfaction of Engineering Incharge.
Approved Waterproofing manufacturer has to provide supporting technical submittals, calculations along with the bid submission. Approvals and go ahead by the Engineering Incharge on methodology is a must to proceed further.
Manufacturer shall share the compliance certificate as per specifications & also share third party test and Data sheet shall have minimum specified range. Any deviation from the specifications will have financial concequency
Products used by the contractors to be of low VOC and in line with IGBC requirements.
Consumption of waterproofing shall be established at site and third party, manufacturer shall share density, solild content data in MTC & TDS.
The Client has provided reuirement for the preferred waterproofing methods for the items listed in this BoQ, the Contractor is expected to propose a suitable water proofing method and provided detailed item description, Work Method Statement, Product Details of the proposed materials along with their technical details with the proposal.

## Specifications Clauses
General Specification Clause
Location : Unconfined Retaining Wall Solutions
Option 1 : SBS Membrane : Shallow Basements
Supplying and installing waterproofing treatment by using 2 mm thick self-adhesive SBS-modified bitumen membrane, applied over a primed retaining wall surface, terminated and sealed at top and bottom as per drawings, and protected with a minimum 6–8 mm thick geotextile-backed HDPE dimple board. Membrane shall be installed in strict accordance with manufacturer’s recommendations and shall provide an intimate bond with the substrate to resist water ingress and lateral migration. The 2 mm SBS modified bitumen membrane shall be a multi-layer composite film comprising a resilient bituminous sheet with a self-adhesive polymeric layer, designed for high flexibility, crack-bridging, and durability against hydrostatic pressure. Installation shall ensure all side laps (≥100 mm) and end laps (≥150 mm) are sealed firmly with pressure or heat bonding. The item rate shall include base preparation comprising wire-brushing the concrete surface, cleaning with oil-free compressed air, and rectification of construction joints, cracks, and honeycombs with polymer-modified mortar as per approved methodology. Scope shall also include supply and application of compatible primers, detailing of terminations, fixing of geotextile-backed HDPE dimple board for protection, and QA/QC checks for continuity and thickness. Item rates shall cover all materials, consumables, labour, transport, tools, plant, curing, scaffolding, incidental charges, and testing costs, as required by specifications, drawings, and the Engineer-in-Charge. The waterproofing contractor shall provide a 10-year performance guarantee on approved stamp paper covering the complete system. Mode of Measurement: As per drawing dimensions of treated area; overlaps deemed included in the rate.
Option 2 :1K PU Membrane: Shallow to Moderate Basements
Supplying and applying waterproofing treatment by using a one-component, moisture-cured polyurethane (PU) liquid-applied membrane, applied over an epoxy-based primer on retaining wall surfaces, terminated and sealed at top and bottom as per drawings, and protected with 6–8 mm thick geotextile-backed HDPE dimple board or rigid protection board prior to backfilling. The 1K PU membrane shall be applied by brush/roller or spray in multiple coats to achieve a dry film thickness (DFT) of 1.5–2.0 mm, forming a seamless, elastomeric, crack-bridging waterproofing layer. The PU system shall comply with relevant ASTM standards (ASTM D412 for tensile/elongation, ASTM D903 for adhesion, ASTM D5385 for hydrostatic resistance) and shall be UV-resistant or suitably protected against sunlight and mechanical damage. The item rate shall include base preparation comprising grinding/wire-brushing, moisture removal (≤5%), cleaning with oil-free compressed air, repairing honeycombs and cracks with polymer-modified mortar, and application of primer. Scope shall also include multiple coats of PU membrane applied to specified thickness, detailing at grooves, corners, and penetrations, provision of protection layers, QA/QC checks, curing, and full documentation. Item rates shall cover all materials, consumables, labour, transport, scaffolding, tools & plant, curing, incidental charges, and QA/QC testing costs, as required by specifications, drawings, and Engineer-in-Charge. The waterproofing contractor shall provide a 10-year performance guarantee on approved stamp paper covering the entire PU system. Mode of Measurement: As per drawing dimensions of net treated surface; overlaps and terminations deemed included in the rate.
Option 3 :2K PU Membrane: Deep Basements
Supplying and applying waterproofing treatment by using a two-component, spray-applied polyurethane elastomeric membrane, applied over a compatible moisture-tolerant epoxy/PU primer on retaining wall surfaces, terminated and sealed as per drawings, and protected with 6–8 mm geotextile-backed HDPE dimple board or rigid protection board prior to backfilling. The 2K PU membrane shall be applied by plural-component spray equipment in multiple passes to achieve a seamless, continuous coating with DFT of 2.0–2.5 mm. The system shall exhibit elongation ≥400% and tensile strength ≥2.5 MPa (ASTM D412), with crack-bridging capacity ≥2.0 mm and hydrostatic resistance ≥10 bar (ASTM D5385). The elastomeric spray membrane shall be designed for deep basements subject to high hydrostatic pressure, structural movement, and aggressive backfill conditions, forming a fully bonded, monolithic waterproofing layer. The item rate shall include surface preparation (grinding/cleaning, moisture ≤5%, crack/honeycomb rectification), application of primer, spray application by approved high-pressure plural-component equipment, edge/junction detailing, protection installation, QA/QC checks, curing, and documentation. Item rates shall cover all materials, equipment mobilization, consumables, labour, plant & machinery, scaffolding, curing, incidental charges, and testing costs, as required by specifications, drawings, and Engineer-in-Charge. The contractor shall provide a 10-year waterproofing guarantee on non-judicial stamp paper covering the full PU spray system. Mode of Measurement: Net surface area of retaining wall treated, as per drawings; overlaps and detailing deemed included in rates.
Option 4 :Coal Tar Epoxy
Supplying and applying waterproofing and protective coating by using a coal-tar–modified epoxy high-solids system, applied in two coats over a compatible epoxy primer, on retaining wall surfaces up to Finished Floor Level (FFL) as shown in drawings. The system shall be designed to provide a dense, chemical-resistant, and impermeable coating suitable for basements in aggressive environments such as sewage, saline water, or acidic groundwater conditions. The system shall achieve a minimum DFT of 300 μm (primer ~100 μm + coal tar epoxy ≥200 μm), with properties conforming to ASTM standards for adhesion, abrasion resistance, and chemical resistance. Application shall be carried out strictly as per manufacturer’s guidelines, ensuring full coverage, continuity across corners, edges, grooves, and terminations. The item rate shall include surface preparation by mechanical grinding and air cleaning, moisture control (≤5%), repairing cracks and honeycombs, application of primer, uniform application of coal tar epoxy coating in required thickness, curing, QA/QC checks, and documentation. Item rates shall cover all materials, consumables, labour, scaffolding, equipment, curing, transport, and incidental charges as required by drawings and Engineer-in-Charge. The contractor shall provide a 10-year performance guarantee on non-judicial stamp paper covering the complete coal tar epoxy system. Mode of Measurement: Net surface area of retaining wall treated as per drawings; overlaps and terminations deemed included.
Option 5 :Crystalline Coatings
Supplying and applying crystalline waterproofing coating in slurry form, brush-applied in two coats to retaining wall concrete surfaces, designed to penetrate capillaries and form insoluble crystals that block water migration. The crystalline system shall provide integral waterproofing by permanently filling pores, micro-cracks, and capillaries, and shall be suitable for positive side or negative side application where direct membrane installation is not feasible. The crystalline coating shall be mixed with potable water and applied at a coverage rate recommended by the manufacturer, ensuring even application to a pre-wetted but surface-dry substrate. The system shall demonstrate resistance to hydrostatic pressure ≥7 bar (ASTM D5385), adhesion ≥1.0 MPa (ASTM D4541), and no water penetration as per EN 12390-8. The item rate shall include surface preparation (wire-brushing, air cleaning, pre-wetting), preparation of slurry, application in two coats, curing with light water spray, QA/QC checks, and documentation. Item rates shall cover all materials, consumables, labour, transport, scaffolding, curing, and incidental charges as required by specifications, drawings, and Engineer-in-Charge. The waterproofing contractor shall provide a 10-year performance guarantee on non-judicial stamp paper covering the crystalline coating system. Mode of Measurement: Net treated area as per drawings; overlaps deemed included.

## BOQ Items
BILL OF QUANTITY
| Items | Unit | Quantity | Unit Rate (INR) | Amount (INR)
Basements : Unconfined Retaining Wall Waterproofing
Option 1 : SBS Membrane : Shallow Basements
1.1 | Surface preparation: mechanical wire-brushing, air cleaning, rectification of cracks, honeycombs, and joints with polymer-modified mortar. | SQM | 0 | 0 | 0
1.2 | Supplying and applying compatible primer coat on prepared concrete surface to receive SBS membrane. | SQM | 0 | 0 | 0
1.3 | Supplying and installing 2 mm thick self-adhesive SBS-modified bitumen membrane, including sealing of side laps (≥100 mm) and end laps (≥150 mm), with full continuity at corners and edges. | SQM | 0 | 0 | 0
1.4 | Supplying and fixing 6–8 mm thick geotextile-backed HDPE dimple board for protection of membrane prior to backfilling. | SQM | 0 | 0 | 0
Option 2 :1K PU Membrane: Shallow to Moderate Basements
2.1 | Surface preparation: grinding/wire-brushing, moisture ≤5%, air cleaning, rectification of cracks, honeycombs, and joints with polymer-modified mortar. | SQM | 0 | 0 | 0
2.2 | Supplying and applying epoxy-based primer compatible with PU membrane, applied uniformly as per TDS. | SQM | 0 | 0 | 0
2.3 | Supplying and applying 1K moisture-cured PU membrane, applied by brush/roller/spray in two or more coats to achieve DFT 1-1.5mm, seamless and elastomeric. | SQM | 0 | 0 | 0
2.4 | Detailing at grooves, corners, covings, and pipe penetrations using compatible sealants or reinforcing fabric. | SQM | 0 | 0 | 0
2.5 | Supplying and fixing 6–8 mm geotextile-backed HDPE dimple board / rigid protection board to safeguard PU membrane prior to backfilling. | SQM | 0 | 0 | 0
Option 3 :2K PU Membrane: Deep Basements
3.1 | Surface preparation: mechanical grinding, moisture ≤5%, removal of laitance, cleaning with compressed air, rectification of cracks and honeycombs. | SQM | 0 | 0 | 0
3.2 | Supplying and applying compatible epoxy/PU primer on prepared surface, as per manufacturer’s TDS. | SQM | 0 | 0 | 0
3.3 | Supplying and applying 2K spray-applied PU membrane, installed by plural-component spray equipment in multiple passes to achieve DFT 2.0 mm, seamless and monolithic. | SQM | 0 | 0 | 0
3.4 | Junction, groove, and pipe penetration detailing using PU sealants, waterbars, or reinforcing fabrics. | SQM | 0 | 0 | 0
| Supplying and fixing 6–8 mm geotextile-backed HDPE dimple board / rigid protection board for protection against backfill pressure. | SQM | 0 | 0 | 0
Option 4 :Coal Tar Epoxy
4.1 | Surface preparation: mechanical grinding, cleaning, moisture ≤5%, rectification of cracks, voids, and honeycombs with polymer-modified mortar. | SQM | 0 | 0 | 0
4.2 | Supplying and applying epoxy primer on prepared surface, DFT ~100 μm, ensuring uniform coverage. | SQM | 0 | 0 | 0
4.3 | Supplying and applying coal-tar–modified epoxy high-solids coating, applied in two coats to achieve a minimum DFT of 200 μm, forming a dense and impermeable protective film. | SQM | 0 | 0 | 0
4.4 | Detailing at grooves, edges, corners, and penetrations to ensure continuity of coating. | RM | 0 | 0 | 0
Option 5 :Crystalline Coatings
5.1 | Surface preparation: mechanical wire-brushing, air cleaning, and pre-wetting substrate to saturated surface-dry condition. | SQM | 0 | 0 | 0
5.2 | Supplying and mixing crystalline waterproofing powder with potable water to form slurry, as per manufacturer’s instructions. | SQM | 0 | 0 | 0
5.3 | Applying crystalline slurry in two coats by brush or spray, ensuring complete coverage of surface and junctions. | SQM | 0 | 0 | 0
5.4 | Detailing at construction joints, grooves, and corners with crystalline slurry or crystalline mortar. | RM | 0 | 0 | 0

## Reference Standards
Reference Standards
Location : Unconfined Retaining Wall Solutions
Standard | Detail | Note
ASTM D 412 | Tensile Strength & Elongation: | Measures flexibility and crack-bridging capacity of membranes.
ASTM D903 | Peel Adhesion | Assesses bond strength of membranes to concrete or substrate.
ASTM D 5385 | Hydrostatic Pressure Resistance | Evaluates ability of waterproofing to resist water penetration under pressure.
ASTM C836 | Liquid-Applied Membranes: | Specifies performance criteria for cold, liquid-applied waterproofing systems.
IS 16471 | Waterproofing for Basements | Guidance for below-grade waterproofing design and application in Indian conditions.

## Performance Parameters
Performance Standard
Location : Unconfined Retaining Wall Solutions
Property | SBS Membrane | 1K PU Membrane | 2K PU Membrane | Coal Tar Epoxy | Crystalline Coating
Elongation | ≥150% (ASTM D412) | ≥250%-400% (ASTM D412) | ≥400%-500% (ASTM D412) | Rigid | Rigid
Tensile Strength | ≥1.5 MPa | ≥1.5 MPa | ≥2.5 MPa | Limited | Limited
Crack Bridging | ≥0.6 mm | ≥1.0-2.0 mm | ≥2.0 mm | Limited | Hairline (<0.3mm)
DFT | 2 mm (nominal) | 1.5–2.0 mm | 2.0–2.5 mm | ≥300 μm DFT | ~1 kg/m² (2 coats)
Adhesion to Concrete | ≥0.5 N/mm (ASTM D903) | ≥1.0 MPa | ≥1.5 MPa | ≥1.5 MPa | ≥1.0 MPa
Hydrostatic Resistance | 5 bar | 7 bar | 10 bar
Chemical Resistance | Moderate | Good | Good | Excellent | Mild sulfates, chlorides
Suitability | Shallow, open basements | Shallow to Moderate Basements | Deep basements | Shallow, chemical exposure | Ancillary / repair / negative side

## Checklist
Checklist
Location : Unconfined Retaining Wall Solutions
S No | Description | Yes | No
1 | Material Delivery
Materials received with intact packaging, valid shelf life, and MTCs
2 | Substrate & Primer
Surface ground & vacuum-cleaned; moisture ≤5%
Defects (cracks/honeycombs) repaired
Construction Joints in Retaining Wall treatments
Primer for SBS membrane/ PU Membrane/ Coal Tar Epoxy applied as per TDS
3 | Coating Application
Membrane installed at specified thickness/DFT
Laps sealed & joints tested (SBS)
Continuous film without pinholes/voids (PU)
Substrate repaired, dry (SBS/Coal Tar).
Overlaps welded/tested (SBS).
Spray PU thickness recorded.
Coal tar epoxy mixed mechanically; ≥2 coats.
Crystalline applied on SSD surface, cured ≥3 days.
4 | Post Application
Minimum 72 h cure completed before backfill/traffic
Area inspected/accepted by waterproofing contractor/Engineer
Geotextile/dimple protection installed before backfill
Minimum curing time observed
QA/QC tests documented